BESS OPTIMIZER

Validation  ·  Key Inputs  ·  Sensitivity Analysis

How to verify results, what data matters most, and what changes the answer

| PART 1 | PART 2 | PART 3 |
| --- | --- | --- |
| Validation | Key Inputs | Sensitivity |

PART 1

HOW TO EVALUATE WHETHER THE SIMULATION RESULT IS CORRECT

# 1.1  The Three Levels of Validation

Validating an optimizer result means checking three different things in order. Do not skip to level 3 without passing levels 1 and 2 — a mathematically correct result can still be physically wrong if the inputs are bad.

| Level | Name | Question to Answer |
| --- | --- | --- |
| Level 1 | Mathematical validity | Did Gurobi actually satisfy all constraints? Are the numbers internally consistent? |
| Level 2 | Physical plausibility | Do the results make real-world sense? Are hourly flows physically possible? |
| Level 3 | Economic reasonableness | Is the financial result believable given the site characteristics? |

## 1.2  Level 1 — Mathematical Validity Checks

Run these checks on the optimizer output data before trusting any result:

### Check 1.1 — Energy Balance (Power Balance)

For every single hour in your CSV output, this equation must hold to within floating point tolerance (< 0.01 kW):

solar[t] + discharge[t] + grid_import[t] = load[t] + ch_solar[t] + ch_grid[t] + solar_export[t] Tolerance: difference < 0.01 kW in every hour How to check in Python: df['balance_error'] = (df['solar'] + df['discharge'] + df['grid_import'] - df['load'] - df['ch_solar'] - df['ch_grid'] - df['solar_export']) assert df['balance_error'].abs().max() < 0.01, 'Power balance violated!'

### Check 1.2 — SOC Continuity

The state of charge must follow the energy balance equation exactly. Verify hour by hour:

soc_reconstructed[t] = soc_reconstructed[t-1] + ch_solar[t-1] * eta_charge - discharge[t-1] / eta_discharge soc_reconstructed[0] = E_max * 0.5 (initial condition) Check: max( ¦soc_output[t] - soc_reconstructed[t]¦ ) < 0.1 kWh If this fails → SOC dynamics constraint was violated → result is wrong.

### Check 1.3 — No Simultaneous Charge and Discharge

In the MILP model, u[t] binary prevents this. Verify it held:

For every hour t: NOT (ch_solar[t] > 0.1 AND discharge[t] > 0.1) How to check: violations = df[(df['ch_solar'] > 0.1) & (df['discharge'] > 0.1)] print(f'Simultaneous charge+discharge violations: {len(violations)}') # Should be 0

### Check 1.4 — No Simultaneous Import and Export

z[t] binary enforces this. Verify:

For every hour t: NOT (grid_import[t] > 0.1 AND solar_export[t] > 0.1) violations = df[(df['grid_import'] > 0.1) & (df['solar_export'] > 0.1)] # Should be 0

### Check 1.5 — SOC Bounds

Battery must always stay within its physical limits:

soc_min = E_kwh * soc_min_pct soc_max = E_kwh * soc_max_pct assert df['soc'].min() >= soc_min - 0.1 assert df['soc'].max() <= soc_max + 0.1 If violated → constraint C7 or C6 was not applied correctly.

### Check 1.6 — Annual Energy Conservation

Total energy in = total energy out over the year, accounting for losses:

Annual totals: total_load = sum(load[t]) total_solar = sum(solar[t]) total_import = sum(grid_import[t]) total_export = sum(solar_export[t]) total_charge = sum(ch_solar[t]) total_discharge = sum(discharge[t]) Check 1: total_solar + total_import ≈ total_load + total_export + total_charge (all solar and import accounted for as load, export, or stored) Check 2: total_discharge ≈ total_charge × eta_charge × eta_discharge (what went in × round-trip efficiency came back out) Tolerance: ±5% (SOC start/end difference can cause small deviation)

## 1.3  Level 2 — Physical Plausibility Checks

These checks use your knowledge of the real site to verify the optimizer's decisions make physical sense.

### Check 2.1 — Self-Sufficiency Sanity

Rule: Self-sufficiency cannot exceed the theoretical maximum.

max_theoretical_self_suff = (direct_solar_to_load + solar_surplus × eta_roundtrip) / total_load direct_solar_to_load = sum(min(solar[t], load[t])) solar_surplus = sum(max(0, solar[t] - load[t])) eta_roundtrip = eta_charge × eta_discharge (e.g. 0.95 × 0.95 = 0.9025) If reported self-sufficiency > max_theoretical → RESULT IS WRONG.

### Check 2.2 — Battery Cycles per Year (Sanity Check)

annual_cycles = total_discharge / E_kwh Expected range: Solar-only (green battery): 150 – 350 cycles/year Grid+solar battery: 200 – 500 cycles/year Pure arbitrage battery: 300 – 700 cycles/year If annual_cycles < 50: Battery is too large — it rarely discharges If annual_cycles > 1000: Battery is unrealistically small or overworked

### Check 2.3 — Peak Power Check

max_charge_power = max(ch_solar[t]) for all t max_discharge_power = max(discharge[t]) for all t Both must be ≤ P_kw (the reported optimal power capacity) Also check: max_charge_power ≤ max(solar[t] - load[t]) (cannot charge faster than the solar surplus in any hour)

### Check 2.4 — Green Battery Validation (if using green mode)

If green mode is active: sum(ch_grid) must = 0.0 for all hours Also verify: charge only happens during surplus hours surplus_hours = df[df['solar'] > df['load']] non_surplus_charge = df[df['solar'] <= df['load']]['ch_solar'].sum() assert non_surplus_charge < 0.1 (should be near zero)

### Check 2.5 — Negative Price Hours

negative_price_df = df[df['export_price'] < 0] During negative price hours, check: solar_export should be ≈ 0 (optimizer avoids exporting) ch_solar should absorb available surplus instead max_export_during_neg_price = negative_price_df['solar_export'].max() # Should be near 0 — only unavoidable surplus (battery full) goes to grid

## 1.4  Level 3 — Economic Reasonableness Checks

### Check 3.1 — Simple Payback Sanity

upfront_capex = battery_cost_eur_per_kwh × E_kwh annual_savings = baseline_cost - net_annual_cost simple_payback = upfront_capex / annual_savings (years) Typical reasonable range: 5 – 15 years If payback < 3 years: Check if savings are overestimated If payback > 20 years: Battery likely not economical — check inputs If annual_savings < 0: y=0 should have been selected (no battery)

### Check 3.2 — Cost per kWh Stored

cost_per_kwh_stored = ann_capex / total_discharge Typical range: €0.08 – €0.25 / kWh Compare to: import_price - what battery actually saves per kWh value_per_kwh = (total_import_saved × import_price) / total_discharge If cost_per_kwh_stored > value_per_kwh → battery loses money per cycle

### Check 3.3 — Compare Against Greedy Simulation

The most powerful validation: run a simple greedy algorithm independently and compare. If results are very different, investigate why.

Simple greedy (Python, no optimizer needed): soc = E_kwh * 0.5 total_import_greedy = 0 for t in range(8760): surplus = max(0, solar[t] - load[t]) deficit = max(0, load[t] - solar[t]) if surplus > 0: ch = min(surplus, P_kw, (E_kwh - soc) / eta_charge) soc += ch * eta_charge else: dis = min(deficit, P_kw, (soc - soc_min) * eta_discharge) soc -= dis / eta_discharge total_import_greedy += deficit - dis greedy_self_suff = 1 - total_import_greedy / total_load Expected: optimizer self-sufficiency ≥ greedy self-sufficiency (optimizer is globally optimal, greedy is myopic) A large gap (>10%) suggests optimizer found real value the greedy missed.

## 1.5  Validation Scorecard

| # | Check | Method | Pass Condition | Priority |
| --- | --- | --- | --- | --- |
| 1.1 | Power balance every hour | CSV calculation | Error < 0.01 kW | CRITICAL |
| 1.2 | SOC reconstruction | CSV calculation | Error < 0.1 kWh | CRITICAL |
| 1.3 | No simultaneous ch+dis | CSV filter | 0 violations | HIGH |
| 1.4 | No simultaneous imp+exp | CSV filter | 0 violations | HIGH |
| 1.5 | SOC within bounds | CSV min/max | No breach | CRITICAL |
| 1.6 | Annual energy conservation | Sum totals | ±5% balance | HIGH |
| 2.1 | Self-sufficiency ≤ theoretical max | Formula | SS ≤ max | CRITICAL |
| 2.2 | Annual cycles in range | Formula | 50–1000 | MEDIUM |
| 2.3 | Peak power ≤ P_kw | CSV max | No breach | HIGH |
| 2.4 | Green: no grid charging | CSV sum | ch_grid = 0 | HIGH (if green) |
| 2.5 | Export ≈ 0 during neg prices | CSV filter | Near zero | MEDIUM |
| 3.1 | Simple payback 5–15 years | Formula | Reasonable range | MEDIUM |
| 3.2 | Cost per kWh stored | Formula | €0.08–0.25/kWh | MEDIUM |
| 3.3 | Compare to greedy | Python script | Optimizer ≥ greedy | HIGH |

PART 2

KEY INPUTS — WHAT DATA MUST BE ACCURATE TO GET A RELIABLE RESULT

# 2.1  Input Quality Hierarchy

Not all inputs affect the result equally. This hierarchy shows which inputs to get right first:

| Tier | Input | Impact on Result | How to Get It Right |
| --- | --- | --- | --- |
| TIER 1 | load_demand (hourly) | Determines battery size by ±30–50% | Smart meter data, 1-year minimum, actual kW not kWh |
| TIER 1 | solar_yield (hourly) | Determines available solar surplus — core sizing driver | Measured generation data preferred over simulated PVsyst output |
| TIER 1 | export_price (hourly) | Changes dispatch strategy and ROI by ±40% | Actual espot market data, same year as load/solar |
| TIER 2 | battery_cost (€/kWh) | Directly scales CAPEX — affects payback period | Get real quotes, not catalogue prices |
| TIER 2 | import_price (€/kWh) | Determines value of avoided grid import | Check if it includes network charges and taxes |
| TIER 2 | lifetime_yrs | Affects CRF — changes annual cost by ±15% | Use manufacturer warranty period as conservative estimate |
| TIER 2 | discount_rate | Affects CRF — see Section 2.3 | Use weighted average cost of capital (WACC) |
| TIER 3 | eta_charge / eta_discharge | Affects cycle value by ±5–10% | 0.95/0.95 is standard LFP. Use 0.90 for conservative |
| TIER 3 | c_rate | Affects P sizing — usually not critical | 0.5C is standard (2h battery). Check with supplier |
| TIER 3 | soc_min / soc_max | Affects usable capacity by ±15% | 0.10/0.95 is standard. Check battery warranty conditions |
| TIER 3 | e_max_kwh (size cap) | Only limits if optimizer hits the cap | Set to realistic site limit — physical space, grid capacity |

## 2.2  Tier 1 Input — Load Demand Data

This is the single most important input. Errors here propagate through everything.

### What you need

- Hourly resolution (1-hour intervals) — 8760 rows for a full year

- Units: kW (average power during each hour), NOT kWh totals

- At least one full calendar year — seasonal patterns matter critically

- Data from the same year as your solar and price data

### Common data quality problems

| Problem | Effect on Result | How to Fix |
| --- | --- | --- |
| Missing hours (NaN values) | Battery sized for wrong total load | Interpolate from adjacent hours or same weekday |
| Monthly totals converted to hourly averages | Loses peak demand spikes — battery undersized | Get actual interval data from smart meter |
| Load from a non-representative year | Battery sized for unusual consumption | Use 3-year average if possible, or weather-correct |
| Units are kWh instead of kW | Everything appears 1x (fine if 1h intervals) | Confirm: sum should equal annual consumption |
| Wrong timezone alignment with solar | Surplus/deficit hours mismatched | Align all data to same UTC offset |
| Includes EV charging or unusual load | Battery oversized for rare peaks | Exclude or flag abnormal load periods |

WARNING: A constant flat load profile (e.g. exactly 70 kW every hour) is NOT realistic. It eliminates intraday load variation which the battery could exploit. Always use actual measured interval data — never substitute with averages. A flat profile will UNDERESTIMATE the optimal battery size by 20–40%.

## 2.3  Tier 1 Input — Solar Yield Data

### Measured vs Simulated Solar Data

| Source | Accuracy | When to Use |
| --- | --- | --- |
| Inverter logs (actual) | Highest — real generation | Best choice when available |
| PVsyst / Solargis simulation | Good — ±5–10% annual error | Use for new installations not yet built |
| ERA5 / satellite irradiance | Moderate — needs plant model | Use to cross-check inverter data |
| Rule-of-thumb estimates | Poor — ±20–40% error | Never use for investment decisions |

### Solar capacity factor check

capacity_factor = total_annual_solar_kwh / (solar_kw_installed × 8760) Expected ranges by location: Germany (north): 0.09 – 0.11 (900–1100 kWh/kWp/year) Germany (south): 0.11 – 0.13 (1100–1300 kWh/kWp/year) Spain: 0.17 – 0.21 (1700–2100 kWh/kWp/year) Middle East: 0.22 – 0.26 (2200–2600 kWh/kWp/year) If your calculated capacity factor is outside these ranges → check data

## 2.4  Tier 1 Input — Export Price (Espot Market)

### Why hourly prices change everything

Unlike a fixed export tariff, hourly espot prices create a fundamentally different dispatch strategy. The optimizer must simultaneously balance:

- High price hours → export solar surplus NOW, even if battery not full

- Low price hours → store in battery instead of exporting

- Negative price hours → absorb all surplus, export nothing

### Data requirements

- Same year, same timezone as load and solar data

- Units must be €/kWh — EPEX Spot publishes in €/MWh. Divide by 1000 if needed

- Negative values must be preserved — do NOT clip to zero

- Check for outliers: Germany espot typically ranges from −€0.50 to +€0.50/kWh

COMMON MISTAKE: EPEX Spot data is published in €/MWh. If you paste it directly into the CSV without dividing by 1000, every price appears 1000× too high. This makes the optimizer massively over-invest in the battery. Check: average German espot price should be roughly €0.05–€0.15/kWh. If your average is €50–€150, you have a unit error.

## 2.5  Tier 2 Input — Battery Cost and Financial Parameters

### Battery cost (€/kWh)

| Battery Type | Typical Cost Range 2024–2025 | Notes |
| --- | --- | --- |
| LFP (commercial, >100 kWh) | €200–€350/kWh | Most common for BESS, use this range |
| LFP (large, >1 MWh) | €150–€250/kWh | Economies of scale apply |
| NMC (legacy) | €250–€400/kWh | Higher energy density, shorter life |
| Installed + BMS + inverter | Add 30–60% to cell cost | Always use all-in installed cost |

### Discount rate — what rate to use

Discount rate = your cost of capital for this investment Typical values: Corporate (low risk): 4–6% → CRF(10yr) = 0.122–0.136 Corporate (medium risk): 7–9% → CRF(10yr) = 0.142–0.156 Corporate (high risk): 10–15% → CRF(10yr) = 0.163–0.199 Project finance / PPA: 5–8% → CRF(10yr) = 0.129–0.149 Using 8% (CRF = 0.149) for a 10-year battery is a common baseline. If uncertain, run the model at 6%, 8%, and 12% to bracket the answer.

### Import price — what to include

The import_price should reflect the TRUE all-in cost of grid electricity: Base energy price: €0.10 – €0.25/kWh Network / distribution: €0.04 – €0.08/kWh Taxes and levies: €0.05 – €0.15/kWh ───────────────────────────────────────────── Total all-in (Germany): €0.20 – €0.45/kWh typical IMPORTANT: If the battery avoids grid import, it saves the FULL all-in price. Using only the energy component underestimates battery savings by 30–50%. Use your actual electricity bill rate, not spot prices, for import_price.

PART 3

SENSITIVITY ANALYSIS — WHAT CHANGES THE ANSWER AND BY HOW MUCH

# 3.1  Sensitivity Overview

A sensitivity analysis systematically varies one input at a time while holding all others constant, then observes how the output (optimal battery size and annual savings) changes. This tells you which inputs to be most careful about — and which don't matter much.

| Input Parameter | −20% change | Base | +20% change | Impact Level |
| --- | --- | --- | --- | --- |
| Import price | −35% E | Base | +40% E | CRITICAL — most sensitive |
| Battery cost (€/kWh) | +25% E | Base | −20% E | CRITICAL |
| Export price level | −15% E | Base | +15% E | HIGH |
| Load demand (annual) | −20% E | Base | +20% E | HIGH |
| Solar yield (annual) | −15% E | Base | +12% E | HIGH |
| Lifetime (years) | −15% E | Base | +12% E | MEDIUM |
| Discount rate | +8% E | Base | −7% E | MEDIUM |
| Round-trip efficiency | −5% E | Base | +5% E | LOW |
| C-rate | ±P only | Base | ±P only | LOW — affects P not E |
| SOC min/max | +3% E | Base | −3% E | LOW |

Note: ±% change in E means the optimal battery size changes by that amount. These are approximate directional estimates — your actual site will differ based on data characteristics.

## 3.2  Sensitivity 1 — Import Price (Most Critical)

The import price determines the value of every kWh the battery shifts away from the grid. It is the single strongest driver of battery economics.

Annual savings ≈ total_discharge × (import_price - cost_per_kwh_stored) If import_price = €0.20/kWh and cost_per_kwh = €0.15/kWh → €0.05 margin If import_price = €0.30/kWh and cost_per_kwh = €0.15/kWh → €0.15 margin Tripling the margin → battery size roughly triples (more storage is profitable) Recommended test: Run at: €0.15, €0.20, €0.25, €0.30, €0.35/kWh Plot E_kwh vs import_price → find the price threshold where battery pays off

### Future import price escalation

This model uses a FLAT import price for all 8760 hours. Real electricity prices typically escalate over time. To account for price escalation, use an adjusted discount rate: real_discount_rate = (1 + nominal_rate) / (1 + price_escalation) - 1 Example: 8% discount rate, 3% annual price escalation real_rate = (1.08) / (1.03) - 1 = 4.85% Use 4.85% as discount_rate in the model This implicitly accounts for future price increases → larger battery justified

## 3.3  Sensitivity 2 — Battery Cost (Second Most Critical)

Optimal battery size scales approximately as: E* ∝ 1 / battery_cost_per_kwh Recommended test values (€/kWh): Optimistic: 150 (large system, competitive tender) Realistic: 250 (current commercial pricing) Conservative: 350 (small system, premium supplier) Future: 80 (projected 2030 price point) Decision rule: calculate break-even battery cost break_even_cost = total_lifetime_savings / E_kwh If actual cost < break_even_cost → invest

Do NOT use cell-only cost (€/kWh from battery manufacturer). Always use INSTALLED system cost including: - Battery cells + BMS - Inverter / PCS - Installation and civil works - Grid connection upgrades (if needed) - Commissioning and first-year O&M Installed cost is typically 1.5× – 2.5× cell cost.

## 3.4  Sensitivity 3 — Solar Yield and Load Profile Shape

It is not just the total annual kWh that matters — the temporal pattern determines how much surplus is available when the battery can absorb it.

### Solar-load coincidence factor

coincidence_factor = sum(min(solar[t], load[t])) / sum(load[t]) High coincidence (>0.6): Battery mainly used for time-shifting remaining surplus Low coincidence (<0.3): Battery used for daily arbitrage — needs to be larger Example: industrial site running 24/7 vs office building 24/7 load: coincidence ≈ 0.35 → moderate battery value Office (9-5): coincidence ≈ 0.55 → strong battery value (solar peak aligns with consumption peak) The optimizer handles this automatically, but knowing the coincidence factor helps interpret why the battery is or isn't large.

### Solar year-to-year variability

Solar generation varies by ±5–15% from year to year due to weather. Recommended approach: 1. Run optimizer with P90 solar year (low irradiance — conservative) 2. Run with P50 solar year (typical / median) 3. Report P50 result as base case, P90 as downside case P90 solar year ≈ P50 × 0.90 (10% below median) Battery sized on P50 will underperform in a P90 year — important for revenue certainty in project finance.

## 3.5  Sensitivity 4 — Export Price Distribution

The SHAPE of the export price distribution matters, not just the average. Two key effects:

### Effect of negative price frequency

Germany espot negative hours: 2019: ~100 hours/year 2022: ~300 hours/year 2023: ~400 hours/year (increasing trend with solar penetration) More negative hours → more curtailment value from battery Battery captures solar that would otherwise cost money to export Run sensitivity: vary neg_price_hours from 100 to 600 Observe: how much does E* increase as negative hours increase? This tells you the value of curtailment protection per kWh of storage.

### Effect of price spikes

High positive price hours (>€0.20/kWh) create discharge opportunities. The optimizer will discharge battery during these hours if economics justify it. Test: remove the top 50 highest-price hours from the export price series Rerun optimizer — observe change in E* and annual savings This shows how much value comes from peak price events vs. average price

## 3.6  Sensitivity 5 — Lifetime and Discount Rate (CRF Sensitivity)

| CRF Table | r = 4% | r = 6% | r = 8% | r = 10% | r = 12% | r = 15% |
| --- | --- | --- | --- | --- | --- | --- |
| n = 7 years | 0.1666 | 0.1791 | 0.1921 | 0.2054 | 0.2191 | 0.2404 |
| n = 10 years | 0.1233 | 0.1359 | 0.1490 | 0.1627 | 0.1770 | 0.1993 |
| n = 12 years | 0.1066 | 0.1193 | 0.1327 | 0.1468 | 0.1614 | 0.1845 |
| n = 15 years | 0.0899 | 0.1030 | 0.1168 | 0.1315 | 0.1468 | 0.1710 |
| n = 20 years | 0.0736 | 0.0872 | 0.1019 | 0.1175 | 0.1339 | 0.1598 |

Key insight: Going from 8% to 12% discount rate increases annual CAPEX by 19% (0.1770/0.1490 = 1.19). For a €300/kWh battery, that is an additional €23/kWh/year. This is often the difference between a project being viable or not.

## 3.7  How to Run a Formal Sensitivity Analysis

A structured approach using the optimizer directly:

### One-at-a-time (OAT) sensitivity

- Fix all inputs at base case values

- Vary one parameter across a range (e.g. import_price = 0.15, 0.20, 0.25, 0.30, 0.35)

- Record E_kwh, P_kw, annual_savings for each run

- Plot: x-axis = parameter value, y-axis = E_kwh and annual_savings

- Repeat for each parameter in the Tier 1 and Tier 2 list

- Rank parameters by their total swing (max E - min E)

### Tornado chart inputs (most impactful parameters first)

Typical tornado chart ranking for BESS (most to least sensitive): 1. Import electricity price (±30–50% swing on E*) 2. Battery installed cost (€/kWh) (±20–30% swing on E*) 3. Annual load demand level (±15–25% swing on E*) 4. Annual solar yield (±10–20% swing on E*) 5. Battery lifetime (years) (±10–15% swing on E*) 6. Export price average level (±5–15% swing on E*) 7. Discount rate (±5–10% swing on E*) 8. Round-trip efficiency (±3–7% swing on E*) 9. C-rate (affects P*, not E*) 10. SOC min/max bounds (±2–5% swing on E*)

## 3.8  Decision Confidence Framework

Use this framework to decide how much to trust the optimizer result before making an investment decision:

| Confidence Level | Conditions | Recommended Action |
| --- | --- | --- |
| HIGH CONFIDENCE | All Tier 1 data from actual measurements. All checks in Part 1 pass. Sensitivity swing on savings < ±20% | Proceed with investment decision. Result is reliable. |
| MEDIUM CONFIDENCE | Tier 1 data partly simulated (e.g. PVsyst). Sensitivity swing ±20–40%. Payback in 7–12 year range | Add 20% contingency to battery cost assumption. Consider phased deployment. |
| LOW CONFIDENCE | Tier 1 data estimated or from non-representative year. Sensitivity swing >40%. Result near breakeven | Do not make investment decision. Collect real data for 3–12 months first. |

# Summary — The Three Most Important Things

1. VALIDATION: The power balance check (Check 1.1) and SOC reconstruction (Check 1.2) are non-negotiable. If these fail, no other result can be trusted. Always export the hourly CSV and verify these two checks first. 2. KEY INPUTS: Get the import electricity price right — it is the single biggest driver. Use the all-in tariff including network charges and taxes. Use actual smart meter data for load, not estimated averages. Make sure export prices are in €/kWh not €/MWh (divide by 1000 if needed). 3. SENSITIVITY: Always run the model at least at three import price scenarios: low (current - 20%), base (current), high (current + 20%). If the battery is economically justified at all three → high confidence. If it only pays off at the high price scenario → risk exists.